CMS Alarm Threshold Review

Drive-train condition monitoring after KR-INC-2026-003

David Chen  ·  28 April 2026  ·  OPS-TEC-0014

# 1. Background

The T-07 gearbox failure at Kestrel Ridge (KR-INC-2026-003) developed over at least eight weeks without triggering a CMS alarm. The ISS bearing envelope kurtosis rose from 3.1 to 4.3; the generic threshold of 4.5 was never reached. This review, carried out by Sara Lindgren with Highline Wind Services and the CMS supplier, sets new thresholds for all Kestrel Ridge turbines and a method for the rest of the fleet.

# 2. Method

Baseline per turbine from 12 months of healthy data (2025).

Warning at baseline + 3σ, alarm at baseline + 5σ, with absolute caps.

Trend alarm: increase of > 25 % in 30 days, independent of the absolute level.

Combine with oil particle count: two indicators in warning → endoscope within 4 weeks.

# 3. New thresholds – Kestrel Ridge

| Indicator | Old warning | Old alarm | New warning | New alarm |
| --- | --- | --- | --- | --- |
| ISS envelope kurtosis | 4.0 | 4.5 | 3.5 | 3.8 |
| ISS envelope RMS (g) | 1.5 | 2.5 | 0.9 | 1.4 |
| HSS envelope RMS (g) | 1.2 | 2.0 | 0.7 | 1.1 |
| Planet stage sideband ratio | – | – | 1.6 | 2.2 |
| Oil particle count (/ml, > 4 µm) | – | – | 600 | 900 |

# 4. Back-test

Applied to the T-07 data, the new warning would have triggered on 3 December 2025 and the alarm on 21 December 2025 – three to six weeks before the failure, enough to plan an up-tower bearing exchange. On T-12 the new thresholds triggered a warning on 9 March 2026, consistent with the endoscope finding.

# 5. False alarm rate

Over the 2025 data set the new thresholds would have raised 11 warnings on healthy turbines (0.6 per turbine per year) and no false alarms. Highline confirmed that this workload is acceptable.

# 6. Fleet roll-out

| Asset | CMS owner | Retuning by |
| --- | --- | --- |
| Kestrel Ridge | Highline / Weyland | Done 2026-04-30 |
| Skerrow Moor | OEM | 2026-10-31 |
| Glenquey | OEM | 2026-11-30 |
| Nordheide, Ostholstein | OEM | 2027-01-31 |
| Dunmore Hill, Wesermarsch | Weyland | 2026-12-15 |
| Thy Vest | OEM | 2027-02-28 |