Battery Energy Storage Systems – Design Guideline

Guideline, Revision 1

Sofie Lindqvist  ·  12 June 2026  ·  WE-ENG-GDL-007

# 1. Purpose

Minimum design requirements for utility-scale BESS. Applies to the 20 MW / 40 MWh system at Millbrook Solar & Storage and to Fenwick Battery Storage (100 MW / 200 MWh). Revision 1 adds lessons from the Millbrook planning process and fire service consultation.

# 2. Cell chemistry and containers

Lithium iron phosphate (LFP) only; NMC is not accepted for utility-scale projects.

Containerised or cabinet systems tested to UL 9540A at cell, module and unit level.

Augmentation strategy defined at FID: either overbuild at day one or planned augmentation in years 6 and 12.

# 3. Fire safety and separation

| Item | Requirement |
| --- | --- |
| Spacing between units | ≥ 3 m or manufacturer's large-scale fire test result, whichever is greater |
| Distance to site boundary | ≥ 25 m to nearest dwelling curtilage |
| Water supply | Hydrant or tank ≥ 228 m³ for 2 h firefighting, agreed with fire and rescue service |
| Detection | Gas (H2, CO) and smoke detection in each unit, deflagration venting |
| Access | Two access points for emergency vehicles, 4 m wide perimeter track |

# 4. Performance

Round-trip efficiency at the point of connection ≥ 85 % at beginning of life. Degradation warranty to state-of-health ≥ 70 % after 7,300 equivalent full cycles or 20 years.

# 5. Grid interface

Grid-forming capability is a scored criterion in every BESS tender from 2026 onwards.

Open point: fire service feedback on Fenwick concept layout expected in Q4 2026.