Utility-Scale Solar PV – Design Guideline

Sofie Lindqvist  ·  27 November 2025  ·  WE-ENG-GDL-010

# 1. Scope

Design principles for ground-mounted PV plants > 20 MWp. Applied first on Millbrook Solar & Storage (85 MWp).

# 2. Key design choices

| Topic | Default | Deviation requires |
| --- | --- | --- |
| Modules | Bifacial mono-PERC/TOPCon, ≥ 580 Wp | Head of Engineering approval |
| Mounting | Single-axis trackers, 1P, backtracking | Yield comparison |
| DC/AC ratio | 1.25–1.35 | Clipping analysis |
| Inverters | Central or string, decided by tender | – |
| Ground clearance | ≥ 0.8 m (sheep grazing) | Ecology input |
| Fencing | Deer fence with mammal gaps every 50 m | – |

# 3. Glint and glare

A glint and glare assessment is required for all receptors within 1 km, including residential properties, roads and aviation. At Millbrook, glare for nearby homes was among the top consultation concerns.

# 4. Biodiversity

Layout shall support at least 10 % biodiversity net gain; Weyland's own target is 20 %, as committed at Millbrook.