## Q&A
# | Date raised | Topic | Question from LTA | Weyland response | Owner | Status
1 | 2025-10-08 | Wind | Justify the choice of ERA5 over MERRA-2 for MCP | ERA5 R² 0.93 vs. 0.89; cross-check result within 0.4 % | Sofie Lindqvist | Closed
2 | 2025-10-13 | Wind | Provide LiDAR validation report (Stage 3) | Uploaded to VDR folder 4.2.1 | Sofie Lindqvist | Closed
3 | 2025-10-18 | Yield | Wake model calibration evidence | Calibration note on three SCADA datasets provided | Sofie Lindqvist | Closed
4 | 2025-10-23 | Yield | Basis for 96.5 % availability | Halden warranted availability + BoP downtime model | Sofie Lindqvist | Closed
5 | 2025-10-03 | Foundations | Status of certification of monopile design | Design basis certified; component certificate due Q1 2026 | Oliver Grant | Closed
6 | 2025-10-08 | Foundations | Contingency for pile refusal in province A | Relief drilling spread on standby, cost in contingency | Oliver Grant | Closed
7 | 2025-11-13 | Electrical | Export cable thermal rating at landfall | HDD section rated with 1.6 K·m/W; DTS installed | Mei Tanaka | Closed
8 | 2025-11-18 | Electrical | Redundancy concept OSS transformers | 2 × 50 % transformers, each 300 MVA | Mei Tanaka | Closed
9 | 2025-11-23 | Supply | Turbine type certificate HTS-12 | Type certificate issued 2025-03, provided | Sofie Lindqvist | Closed
10 | 2025-11-03 | Supply | Cable factory acceptance test regime | FAT per IEC 62067, witnessed by Weyland | Mei Tanaka | Closed
11 | 2025-11-08 | Schedule | Vessel availability for turbine campaign | MV Sea Atlas chartered under WE-CON-2025-040 | Elena Márquez | Closed
12 | 2025-11-13 | HSE | Piling noise mitigation | Bubble curtains for all piles, seasonal restriction | Hannah Weber | Closed
13 | 2025-12-18 | O&M | O&M base readiness | Port of Eastholm lease signed, building 2027 | David Chen | Closed
14 | 2025-12-23 | Grid | Grid compliance simulation models | Provided by Halden, validated against type test | Mei Tanaka | Closed