Solberg Solar Portfolio – Technical Red Flag Memo

3 operating PV plants, 64 MWp, Denmark

Sofie Lindqvist  ·  24 April 2026

# Context

Opportunity screened by Henrik Larsen (Business Development). Three plants in Jutland, commissioned 2019–2021, total 64 MWp. Data room access 6–20 April 2026. Scope limited to red flags only.

# Red flags

Plant 2 (Vestby, 24 MWp): performance ratio dropped from 84 % to 77 % since 2023. Root cause appears to be potential-induced degradation of one module batch – warranty claim not filed by the seller.

Inverter supplier no longer active in Europe; spare parts availability unclear for 41 central inverters.

# Amber

Land lease for Plant 3 ends in 2044 – shorter than the 35-year life assumed in the teaser.

No thermographic inspection since 2022.

# Recommendation

Do not proceed at the indicated price. If the seller provides module test results and a PID remediation plan, a revised bid could be considered. Decision recorded as no-go in the pipeline tracker on 5 May 2026.