Kestrel Ridge – Long-Term Correction Update

Technical note

Sofie Lindqvist  ·  27 February 2026  ·  KR-MET-TN-0005

# 1. Purpose

Update the long-term wind climate at Kestrel Ridge Wind Farm with the on-site met mast KR-MM1 data to the end of 2025, as input to the 2025 operational yield reconciliation and the 2026 budget.

# 2. Data

KR-MM1 (100 m lattice mast, top anemometer at 100 m, vane at 98 m) has been measuring since June 2019. Data availability in 2025 was 97.1 % at 100 m. Two cup anemometers were exchanged during the September 2025 calibration visit; post-calibration offsets were below 0.5 %.

# 3. Results

| Period | Mean wind speed at 100 m (m/s) | Index vs. long term |
| --- | --- | --- |
| 2020 | 8.31 | 100.6 % |
| 2021 | 7.84 | 94.9 % |
| 2022 | 8.42 | 101.9 % |
| 2023 | 8.20 | 99.3 % |
| 2024 | 8.36 | 101.2 % |
| 2025 | 8.33 | 100.8 % |
| Long term (ERA5 2001–2025) | 8.26 | 100.0 % |

2025 was a slightly above-average wind year (+0.8 % in wind speed, about +1.5 % in energy). The actual 2025 generation of 206.6 GWh therefore corresponds to a wind-corrected figure of about 203.5 GWh, which compares to the pre-construction P50 of 204.6 GWh.

# 4. Recommendation

Keep KR-MM1 in operation until at least 2028; it is the only independent reference for the nacelle anemometer drift checks and for the T-07 power curve verification after the gearbox exchange.