## Results
Case | Season | Fenwick export (MW) | Fenwick–Carrbridge loading (%) | Fenwick SGT loading (%) | Voltage at 132 kV (pu) | Result
Winter peak | Winter | 100 | 80.2 | 70 | 1.029 | OK
Winter peak | Winter | 60 | 80 | 61.2 | 0.981 | OK
Winter peak | Winter | -100 | 35.7 | 26 | 0.984 | OK
Summer minimum | Summer | 100 | 86.8 | 70 | 1.018 | OK
Summer minimum | Summer | 60 | 72.1 | 61.2 | 1.006 | OK
Summer minimum | Summer | -100 | 33.9 | 26 | 0.986 | OK
Summer peak wind | Summer | 100 | 95.5 | 70 | 0.975 | OK
Summer peak wind | Summer | 60 | 80.3 | 61.2 | 0.971 | OK
Summer peak wind | Summer | -100 | 47.2 | 26 | 0.979 | OK
Winter peak wind | Winter | 100 | 91.5 | 70 | 1 | OK
Winter peak wind | Winter | 60 | 83.7 | 61.2 | 1.008 | OK
Winter peak wind | Winter | -100 | 55.7 | 26 | 0.982 | OK
N-1 Carrbridge circuit | Summer | 100 | 100.5 | 70 | 0.981 | Overload – constraint needed
N-1 Carrbridge circuit | Summer | 60 | 91.3 | 61.2 | 1 | OK
N-1 Carrbridge circuit | Summer | -100 | 65 | 26 | 1.017 | OK
N-1 SGT1 | Summer | 100 | 106.2 | 95 | 1.005 | Overload – constraint needed
N-1 SGT1 | Summer | 60 | 89.4 | 86.2 | 0.976 | OK
N-1 SGT1 | Summer | -100 | 53 | 51 | 0.971 | OK

## Assumptions
Item | Value
Data pack | NordGrid 2026 Appendix G, issued 3 June 2026
Background generation | Contracted + 3 queued BESS (410 MW)
Tool | PowerFactory 2025 SP2
Study by | Ahmed Rahimi, checked by Mei Tanaka