# Highline Wind Services – Annual Service Report

| Item | Details |
| --- | --- |
| Site / turbine | Kestrel Ridge Wind Farm – T-03 |
| Service type | Annual service (12-month interval) incl. electrical and safety inspection |
| Date | 2026-04-21 |
| Technicians | Stuart Laidlaw, Callum Nisbet, Aileen Brodie |
| Turbine downtime | 28 h |
| Contract | WE-CON-2023-015 (full-service O&M agreement) |
| Work order | HWS-WO-26-1367 |

## 1. Checklist summary

| Check | Result |
| --- | --- |
| Tower flange bolts – 10 % torque check | OK |
| Blade bearing lubrication and seal inspection | OK |
| Pitch accumulators – pre-charge pressure | OK |
| Main bearing grease purge and sample | See findings |
| Gearbox oil sample and filter change | OK |
| Gearbox endoscope (ISS / HSS bearings) | OK |
| Yaw brake pads and yaw gear lubrication | OK |
| Rotor brake caliper and disc | See findings |
| Generator slip ring and brushes | OK |
| Converter cooling circuit and filters | OK |
| HV transformer visual inspection | OK |
| Fire extinguishers and smoke detectors | OK |
| Service lift and fall arrest system | OK |
| Rescue and evacuation kit | OK |
| Aviation lights and ice detection sensor | OK |

## 2. Findings and actions

| Finding | Status |
| --- | --- |
| Pitch accumulator B2 pre-charge 12 % low – recharged | Corrected |
| Minor grease leakage at blade bearing seal, blade A – cleaned, monitor at next visit | Observation |

## 3. Gearbox oil analysis

| Parameter | Result | Limit |
| --- | --- | --- |
| Iron (Fe) | 17 ppm | 50 ppm (warning 35) |
| Water | 240 ppm | 500 ppm |
| Cleanliness (ISO 4406) | 16/14/11 | 19/17/14 |
| Viscosity change at 40 °C | +0.2 % | ±10 % |

## 4. Parts used

Gearbox oil filter element (2×)

Grease cartridges, blade bearings (9×)

Carbon brushes (6×)

## 5. Technician comments

Access to the tower was slow because of soft ground at the crane pad after rain; the access track needs grading. Turbine returned to service and released to the control room after a test run of 30 minutes.

Report reviewed by Ben Okoye (Site Manager, Weyland Energy).