# Highline Wind Services – Annual Service Report

| Item | Details |
| --- | --- |
| Site / turbine | Kestrel Ridge Wind Farm – T-10 |
| Service type | Annual service (12-month interval) incl. electrical and safety inspection |
| Date | 2026-06-09 |
| Technicians | Aileen Brodie, Stuart Laidlaw, Callum Nisbet |
| Turbine downtime | 33 h |
| Contract | WE-CON-2023-015 (full-service O&M agreement) |
| Work order | HWS-WO-26-1629 |

## 1. Checklist summary

| Check | Result |
| --- | --- |
| Tower flange bolts – 10 % torque check | See findings |
| Blade bearing lubrication and seal inspection | OK |
| Pitch accumulators – pre-charge pressure | OK |
| Main bearing grease purge and sample | OK |
| Gearbox oil sample and filter change | OK |
| Gearbox endoscope (ISS / HSS bearings) | OK |
| Yaw brake pads and yaw gear lubrication | OK |
| Rotor brake caliper and disc | OK |
| Generator slip ring and brushes | OK |
| Converter cooling circuit and filters | See findings |
| HV transformer visual inspection | OK |
| Fire extinguishers and smoke detectors | OK |
| Service lift and fall arrest system | See findings |
| Rescue and evacuation kit | OK |
| Aviation lights and ice detection sensor | OK |

## 2. Findings and actions

| Finding | Status |
| --- | --- |
| Paint damage at tower door frame, early corrosion – touch-up applied | Corrected |
| Minor grease leakage at blade bearing seal, blade B – cleaned, monitor at next visit | Observation |
| Converter cabinet filter mats heavily soiled – replaced | Corrected |

## 3. Gearbox oil analysis

| Parameter | Result | Limit |
| --- | --- | --- |
| Iron (Fe) | 13 ppm | 50 ppm (warning 35) |
| Water | 197 ppm | 500 ppm |
| Cleanliness (ISO 4406) | 16/14/11 | 19/17/14 |
| Viscosity change at 40 °C | +0.8 % | ±10 % |

## 4. Parts used

Gearbox oil filter element (2×)

Grease cartridges, blade bearings (7×)

Carbon brushes (6×)

## 5. Technician comments

Work was paused for 3 hours on day 2 because wind speed at hub height exceeded the 15 m/s limit for rotor lock work. Turbine returned to service and released to the control room after a test run of 30 minutes.

Report reviewed by Ben Okoye (Site Manager, Weyland Energy).