Monopile and Transition Piece Specification

Harrow Bay Offshore Wind · Contract WE-CON-2025-027

Sofie Lindqvist  ·  22 July 2025  ·  HB-ENG-SPC-0042

# 1. Scope

This specification defines the technical requirements for the fabrication, coating, inspection and delivery of 40 monopiles and 40 transition pieces under contract WE-CON-2025-027 with Rhenus Steelworks Foundations GmbH. It supplements the Design Basis HB-ENG-BOD-0001 and the approved fabrication drawings.

# 2. Materials

| Component | Grade | Standard | Testing |
| --- | --- | --- | --- |
| Monopile shell plates | S355ML / S420ML | EN 10225-1 | Charpy -40 °C, Z35 through thickness |
| Flanges (forged) | S355NL | EN 10025-3 | UT 100 %, MPI |
| Secondary steel | S355J2 | EN 10025-2 | Type 3.1 cert. |
| Bolts M72 | 10.9 HDG | EN 14399-4 | Lot testing, coating thickness |

# 3. Geometric tolerances

| Item | Tolerance |
| --- | --- |
| Out-of-roundness | ≤ 0.5 % of diameter |
| Straightness over full length | ≤ 0.1 % of length |
| Top flange flatness (after fabrication) | ≤ 1.0 mm |
| Top flange inclination | ≤ 0.5 mm/m |
| Length | + 50 / - 0 mm |

# 4. Welding and NDT

All circumferential and longitudinal welds are submerged arc welded per qualified WPS. NDT scope: 100 % UT (phased array) of all butt welds, 100 % MPI of attachment welds, 10 % TOFD on circumferential welds. Acceptance level per EN ISO 5817 level B. A Weyland resident inspector is present at the Duisburg yard.

# 5. Coating

Transition pieces: three-coat system to ISO 12944 C5-M / CX (zinc-rich epoxy, epoxy, polyurethane topcoat RAL 1023 traffic yellow above +3 m LAT). Monopiles: uncoated below -3 m LAT with cathodic protection; coated in the splash zone.

# 6. Delivery

Delivery ex works Duisburg by sea transport to the Port of Eastholm in batches of six. Each item is delivered with a data book (material certificates, weld maps, NDT reports, dimensional report, coating report).

| Batch | Items | Required at Eastholm |
| --- | --- | --- |
| 1 | HB-A01 – A06 | 2026-03-06 |
| 2 | HB-A07 – A12 | 2026-04-17 |
| 3 | HB-A13 – B04 | 2026-05-08 |
| 4 | HB-B05 – B10 | 2026-08-14 |
| 5 | HB-B11 – C03 | 2026-10-09 |
| 6 | HB-C04 – C09 | 2026-11-20 |
| 7 | HB-C10 – C13 | 2026-12-18 |